## API SPEC
PLC <--> SERVER | Field | STX | HEADER |  | PAYLOAD | [5 empty] | ETX
|  |  | MSG_TYPE | PAYLOAD_LENGTH | DEVICE_ID | CURRENT | VOLTAGE | POWER CONSUMPTION | ENERGY CONSUMPTION | STATUS
1. PLC --> SERVER | Number of Bytes | 2 | 4 | 2 | 2 | 4 | 4 | 4 | 4 | 2 | 1
| Data type | word/short | string | word/short | word/short | float | float | float | float | word/short | byte
| Values | 0x02 | DEEN: Device energy | 20 | 1: MBA1 2: MBA2 3: MBA3 4: MDB1 5: MDB2 6: MDB3 7: MDB4 8: MDB5 9: MDB6 | 0 | 0 | 0 | 0 | 1: Closed 2: Opened 3. Error | 0x03
| Message length | 29
2. SERVER --> PLC | Field |  |  |  | DEVICE_ID | COMMAND
| Number of Bytes |  |  |  | 2 | 2 | 0 | 0 | 0 | 0
| Data type |  |  |  | word/short | word/short
| Values |  | DECO: Device command | 4 | 1: MBA1 2: MBA2 3: MBA3 | 1: Closed 2: Opened
| Message length | 13
3. PLC --> SERVER | Field |  |  |  | DEVICE_ID | RESULT
| Number of Bytes |  |  |  | 2 | 2 | 0 | 0 | 0 | 0
| Data type |  |  |  | word/short | word/short
| Values |  | DERE: Device response | 4 | 1: MBA1 2: MBA2 3: MBA3 | 1: OK 2: NG
| Message length | 13
4. SERVER --> PLC | Field |  |  |  | COMMAND
| Number of Bytes |  |  |  | 2 | 0 | 0 | 0 | 0 | 0
| Data type |  |  |  | word/short
| Values |  | MOCO: Mode command | 2 | 1: Auto 2: Manual
| Total frame size | 11
5. PLC --> SERVER | Field |  |  |  | MODE
| Number of Bytes |  |  |  | 2 | 0 | 0 | 0 | 0 | 0
| Data type |  |  |  | word/short
| Values |  | MORE: Mode response | 2 | 1: Auto 2: Manual
| Message length | 11

## Mapping
D REGISTERS |  |  |  | M REGISTERS
Device name | Description |  |  | Device name | Description
D50 | Status ACB 01
D51 | Status ACB 02
D52 | Status ACB 03
D53 | Status MCCB 01
D54 | Status MCCB 02
D55 | Status MCCB 03
D56 | Status MCCB 04
D57 | Status MCCB 05
D58 | Status MCCB 06
D70 | MODE
D100 | Open connection |  |  | M100 | Open connection status
M101
D110 | DECO DATA
D200 | Close connection
|  |  |  | M110 | STEP 1
|  |  |  | M111 | STEP 2
D300 | Length of data |  |  | M112 | STEP 3
D301 | STX |  |  | M113 | STEP 4
D302 | MSG_TYPE |  |  | M114 | STEP 5
D303 |  |  |  | M115 | STEP 6
D304 | DEVICE_ID |  |  | M116 | STEP 7
D305 | SEQ_NUMBER |  |  | M117 | STEP 8
D306 | CURRENT |  |  | M118 | STEP 9
D307 |  |  |  | M119 | STEP 10
D308 | VOLTAGE |  |  | M120 | STEP 11
D309 |  |  |  | M121 | STEP 12
D310 | POWER_CONSUMPTION |  |  | M122 | STEP 13
D311 |  |  |  | M123 | STEP 14
D312 | ELECTRIC_CONSUMPTION |  |  | M124 | STEP 15
D313 |  |  |  | M125 | STEP 16
D314 | STATUS |  |  | M126 | MANUAL STEP
D315 | ETX |  |  | M127 | DECO STATUS
D500 | Data received
D550 | MSG_TYPE
D600 | Message type QF1 |  |  | M200 | Close connection status
D601 |  |  |  | M201
D602
D603
D604 | Device Id QF1 |  |  | M300 | Sending data status
D605 | Sequence number QF1 |  |  | M301
D606 | Current QF1
D607
D608
D609 |  |  |  | M400
D610 | Voltage QF1
D611 |  |  |  | M500 | Receiving data status
D612 |  |  |  | M501
D613 |  |  |  | M502
D614 | Power consumption QF1
D615
D616
D617
D618 | Electric consumption QF1 |  |  | M600 | Status QF1
D619 |  |  |  | M601 | Status QF2
D620 |  |  |  | M602 | Status QF3
D621 |  |  |  | M603 | Status SF1
D622 |  |  |  | M604 | Status SF2
D623 |  |  |  | M605 | Status SF3
D624 |  |  |  | M606 | Status SF4
D625 |  |  |  | M607 | Status SF5
D626 |  |  |  | M608 | Status SF6
D627 |  |  |  | M609 | Status SF7
D628 |  |  |  | M610 | Status SF8
D629
D630 | Message type QF2
D631
D632
D633
D634 | Device Id QF2
D635 | Sequence number QF2
D636 | Current QF2
D637
D638
D639
D640 | Voltage QF2
D641
D642
D643
D644 | Power consumption QF2
D645
D646
D647
D648 | Electric consumption QF2
D649
D650
D651
D652
D653
D654
D655
D656
D657
D658
D659
D660 | Message type QF3
D661 |  |  |  | M1000 | Socket open button
D662 |  |  |  | M1001 | Not used
D663 |  |  |  | M1002 | Socket Open normally
D664 | Device Id QF3 |  |  | M1003 | Socket Open error
D665 | Sequence number QF3
D666 | Current QF3
D667 |  |  |  | M3000 | Send data button
D668 |  |  |  | M3001
D669 |  |  |  | M3002 | Sending data normal
D670 | Voltage QF3 |  |  | M3003 | Sending data error
D671
D672
D673
D674 | Power consumption QF3
D675
D676
D677
D678 | Electric consumption QF3
D679
D680 |  |  |  | M4000 | Close socket button
D681 |  |  |  | M4001
D682 |  |  |  | M4002
D683 |  |  |  | M4003
D684 |  |  |  | M4004 | Closing flag
D685
D686
D687
D688
D689 |  |  |  | M5002 | Receiving data normal
D690 | Message type SF1 | D810 | Message type SF5 | M5003 | Receiving data error
D691 |  | D811
D692 |  | D812
D693 |  | D813
D694 | Device Id SF1 | D814 | Device Id SF5
D695 | Sequence number SF1 | D815 | Sequence number SF5
D696 | Current SF1 | D816 | Current SF5
D697 |  | D817
D698 |  | D818
D699 |  | D819
D700 | Voltage SF1 | D820 | Voltage SF5
D701 |  | D821
D702 |  | D822
D703 |  | D823
D704 | Power consumption SF1 | D824 | Power consumption SF5
D705 |  | D825
D706 |  | D826
D707 |  | D827
D708 | Electric consumption SF1 | D828 | Electric consumption SF5
D709 |  | D829
D710 |  | D830
D711 |  | D831
D712 |  | D832
D713 |  | D833
D714 |  | D834
D715 |  | D835
D716 |  | D836
D717 |  | D837
D718 |  | D838
D719 |  | D839
D720 | Message type SF2 | D840 | Message type SF6
D721 |  | D841
D722 |  | D842
D723 |  | D843
D724 | Device Id SF2 | D844 | Device Id SF6
D725 | Sequence number SF2 | D845 | Sequence number SF6
D726 | Current SF2 | D846 | Current SF6
D727 |  | D847
D728 |  | D848
D729 |  | D849
D730 | Voltage SF2 | D850 | Voltage SF6
D731 |  | D851
D732 |  | D852
D733 |  | D853
D734 | Power consumption SF2 | D854 | Power consumption SF6
D735 |  | D855
D736 |  | D856
D737 |  | D857
D738 | Electric consumption SF2 | D858 | Electric consumption SF6
D739 |  | D859
D740 |  | D860
D741 |  | D861
D742 |  | D862
D743 |  | D863
D744 |  | D864
D745 |  | D865
D746 |  | D866
D747 |  | D867
D748 |  | D868
D749 |  | D869
D750 | Message type SF3 | D870 | Message type SF7
D751 |  | D871
D752 |  | D872
D753 |  | D873
D754 | Device Id SF3 | D874 | Device Id SF3
D755 | Sequence number SF3 | D875 | Sequence number SF7
D756 | Current SF3 | D876 | Current SF7
D757 |  | D877
D758 |  | D878
D759 |  | D879
D760 | Voltage SF3 | D880 | Voltage SF7
D761 |  | D881
D762 |  | D882
D763 |  | D883
D764 | Power consumption SF3 | D884 | Power consumption SF7
D765 |  | D885
D766 |  | D886
D767 |  | D887
D768 | Electric consumption SF3 | D888 | Electric consumption SF7
D769 |  | D889
D770 |  | D890
D771 |  | D891
D772 |  | D892
D773 |  | D893
D774 |  | D894
D775 |  | D895
D776 |  | D896
D777 |  | D897
D778 |  | D898
D779 |  | D899
D780 | Message type SF4 | D900 | Message type SF8
D781 |  | D901
D782 |  | D902
D783 |  | D903
D784 | Device Id SF4 | D904 | Device Id SF8
D785 | Sequence number SF4 | D905 | Sequence number SF8
D786 | Current SF4 | D906 | Current SF8
D787 |  | D907
D788 |  | D908
D789 |  | D909
D790 | Voltage SF4 | D910 | Voltage SF8
D791 |  | D911
D792 |  | D912
D793 |  | D913
D794 | Power consumption SF4 | D914 | Power consumption SF8
D795 |  | D915
D796 |  | D916
D797 |  | D917
D798 | Electric consumption SF4 | D918 | Electric consumption SF8
D799 |  | D919
D800 |  | D920
D801 |  | D921
D802 |  | D922
D803 |  | D923
D804 |  | D924
D805 |  | D925
D806 |  | D926
D807 |  | D927
D808 |  | D928
D809 |  | D929
D3000 | Data send
D5000